SPRINKLER PLAN submittal FORM

PROPERTY INFORMATION:

| Building Name: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Address: |  |  |  | County: |  |
| Owners Name: |  |  |  |  |  |
| Owners Address: |  |  |  |  |  |
| Owners Phone #: | Fax: |  | E-mail: |  |  |

SYSTEM DESIGNER/CONTRACTOR:

| Company Name |  |  |  | *Illinois F. S. C. # |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Company Address |  |  |  |  |  |  |  |  |
| Contact Person (Designer): |  |  |  |  |  |  |  |  |
| Phone | Fax: | xcvb | E-mail: |  |  |  |  |  |
| Was the System Designed and Stamped by an Illinois Registered Professional Engineer? |  |  |  |  |  | Yes No |  |  |

* Fire Sprinkler Contractor licensing is required in Illinois for NFPA 13, and NFPA 13R systems

GENERAL

Indicate if the installation of the proposed fire sprinkler system is (check all that apply):

| Required by the State-adopted NFPA Life Safety Code |  | Required for equivalency, alternative level of protection, etc. |  |
| --- | --- | --- | --- |
| Required by local ordinances or insurance provider |  | Not required, system is being voluntarily installed |  |
| Other |  |  |  |

NFPA Standard used in the system design and proposed installation:

| NFPA 13 Standard for the Installation of Sprinkler Systems | Edition: _ _ |
| --- | --- |
| NFPA 13R Standard for the Installation of Sprinkler Systems in Residential Occupancies up to and Including Four Stories in Height | Edition: _ _ |
| NFPA 13D Standard for the Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes | Edition: _ _ |

The proposal represents:

A new system being installed in the building	       Modifications to an existing system	      Extension of an existing system

Other: _______________________________________________________________________________________________________

Construction type of building as defined by NFPA Standard #220:

| Fire resistive | Non-combustible | Ordinary | Heavy timber | Wood frame | Mixed |
| --- | --- | --- | --- | --- | --- |

BUILDING USE AND OCCUPANCY CLASSIFICATION

Occupancy classification (per NFPA Life Safety Code):

| Ambulatory health care Apartment Building Assembly Business | Day care center Day care home Detention and correctional Educational | Health care Hotel/dormitory Industrial Lodging or rooming house | Mercantile One- or two-family dwelling Residential board and care Storage |
| --- | --- | --- | --- |

Fire sprinkler occupancy hazard classification:

| Light hazard | Ordinary hazard Group II | Extra hazard Group I | Storage |  |
| --- | --- | --- | --- | --- |
| Special occupancy | Ordinary hazard Group I | Extra hazard Group II |  |  |
| Special occupancy requirements for the system (Flammable/combustible liquids, aircraft hangars, oxidizers, etc.)? |  |  |  | Yes No |

If a storage occupancy, commodity classification:

| Class I |  | Class II |  |  | Class III |  | Class IV |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Group A |  | Group B |  |  | Group C |  |  |  |  |
| Storage over 12 feet? | Yes |  | No |  |  |  |  |  |  |

DESIGN SPECIFICATIONS

| Type of system: |  | Hydraulically calculated |  | Pipe schedule (for areas 5,000 Sq. Ft. or less and existing system only) |  |
| --- | --- | --- | --- | --- | --- |
| Requirements For All Hydraulically Calculated Systems |  |  |  |  |  |
| Yes | No |  | Design area of water application specified |  |  |
| Yes | No |  | Minimum rate of water application (density) specified |  |  |
| Yes | No |  | Area per sprinkler specified |  |  |
| Yes | No |  | Total water requirements as calculated, including allowance for inside hose, outside hydrants, and water curtain and exposure sprinklers, specified |  |  |
| Yes | No | N/A | Limitations (dimension, flow, and pressure) on extended coverage or other listed special sprinklers specified |  |  |
| Additional Requirements For 13 Systems |  |  |  |  |  |
| Yes | No | N/A | Allowance for in-rack sprinklers provided |  |  |
| Additional Requirements For 13R Systems |  |  |  |  |  |
| Yes | No |  | All sprinklers, up to four, within the most hydraulically demanding compartment included in the design area |  |  |
| Yes | No |  | Minimum density at least 0.05 gpm/ft2 to the design sprinklers |  |  |
| Yes | No |  | Areas outside of the dwelling unit, such as garages or lobbies, protected in accordance with the design criteria of NFPA 13 or the specific design criteria of NFPA 13R |  |  |
| Yes | No | N/A | Domestic demand included, as part of the system demand, for systems with common domestic and fire mains |  |  |
| Additional Requirements For 13D Systems |  |  |  |  |  |
| Yes | No |  | All sprinklers, up to two, within the most hydraulically demanding compartment included in the design area |  |  |
| Yes | No |  | Minimum density at least 0.05 gpm/ft2 to the design sprinklers |  |  |
| Yes | No |  | Area per sprinkler specified |  |  |

Is the Following Information Provided on Plans/Specifications?

| Yes | No |  | Total area protected by each system on each floor |
| --- | --- | --- | --- |
| Yes | No |  | Number of sprinklers on each riser per floor |
| Yes | No |  | Piping provisions for flushing |
| Yes | No |  | Hydraulic data nameplate (for hydraulically designed systems) |
| Yes | No |  | Hydraulic reference points shown on the plan that correspond with comparable reference points on the hydraulic calculation sheets |
| Yes | No |  | Most demanding area is calculated |
| Yes | No |  | Pipe sizes and lengths shown on the plan correspond with the sizes and lengths shown on the hydraulic calculation sheets |
| Yes | No |  | Minimum rate of water application (density), design area of water application, in-rack sprinkler demand, and water required for inside and outside hose streams |
| Yes | No |  | Total quantity of water and pressure required noted at a common reference point for each system |
| Yes | No |  | Relative elevations of sprinklers, junction points, and supply or reference points |
| Yes | No |  | Pressure loss for backflow preventer and/or meter included in hydraulic calculations |
| Yes | No | N/A | Total number of sprinklers on each dry pipe, preaction, combined dry pipe-preaction, or deluge system |
| Yes | No | N/A | Approximate capacity (in gallons) of each dry pipe system |
| Yes | No | N/A | Where equipment is to be installed as an addition to an existing system, enough of the existing system indicated to make all conditions clear |
| Additional Requirements For 13 Systems |  |  |  |
| Yes | No | N/A | If room design method is used, all unprotected wall openings throughout the floor protected |
| Additional Requirements For 13D Systems |  |  |  |
| Yes | No |  | The minimum pipe size is ¾ in. piping system |
| Yes | No |  | Minimum rate of water application (density) and design area of water application specified |
| Yes | No | N/A | Devices that restrict flow or reduce pressure, such as filtration or water softening, shown |
| Multi-purpose |  |  |  |
| Yes | No | N/A | If the system is a multipurpose piping system and utilizes ½ in. pipe, the specific design criteria are met for the utilization of this pipe |

SPRINKLER TYPE AND COVERAGE

Type of sprinkler system:

| Wet | Dry |  | Anti-freeze | Preaction |  | Deluge | Pre-Engineered (13D) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Yes | No |  | Sprinklers omitted in any area? |  |  |  |  |  |
| Yes | No | N/A | If yes, allowed per NFPA 13 Omitted area(s) |  |  |  |  |  |
| Yes | No | N/A | If yes, allowed per NFPA 13R Omitted area(s) |  |  |  |  |  |
| Yes | No | N/A | If yes, allowed per NFPA 13D Omitted area(s) |  |  |  |  |  |
| 13D | Yes | No | System is a multipurpose or network system |  |  |  |  |  |
| 13D | Yes | No | All wet piping in areas that are maintained above 40°F |  |  |  |  |  |

Area of coverage:

| Total |  |  | Partial | Special hazard | Other |  |
| --- | --- | --- | --- | --- | --- | --- |
| Yes | No | All wet piping in areas that are maintained above 40° F |  |  |  |  |

FIRE PUMP

| Yes | No | Fire pump provided |  |
| --- | --- | --- | --- |
| Yes | No | Gallon per minute and pressure rating of the pump specified |  |

Type of fire pump:

| Electric |  |  | Diesel | Gasoline | LPG/LNG | Steam |
| --- | --- | --- | --- | --- | --- | --- |
| Yes | No | Pump layout is in accordance with NFPA 20 |  |  |  |  |

WATER SUPPLY

Is the following information provided?

| Yes | No | Water test location |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Yes | No | Date and time of test |  |  |  |
| Yes | No | Static pressure, residual pressure, and flow in gpm |  |  |  |
| Yes | No | Flow test “conducted by” contact information on plans |  |  |  |
| Yes | No | Size of main indicated: |  |  |  |
|  |  | Dead-end main |  | Looped main |  |
| Other sources of water supply, with pressure or elevation: |  |  |  |  |  |

PRIVATE FIRE SERVICE MAINS

Is the following information provided?

| Yes | No | Sizes of mains |  | Yes | No | Sizes, types, and locations of valves |
| --- | --- | --- | --- | --- | --- | --- |
| Yes | No | Pipe lengths |  | Yes | No | Sizes, types, and locations of valve indicators |
| Yes | No | Pipe locations |  | Yes | No | Sizes, types, and locations of regulators |
| Yes | No | Weights |  | Yes | No | Sizes, types, and locations of meters |
| Yes | No | Pipe materials |  | Yes | No | Sizes, types, and locations of valve pits |
| Yes | No | Point of connection to city main |  | Yes | No | Depth of top of pipe laid below grade |

Is the following information provided on plans/specification?

| Yes | No | Scale used |
| --- | --- | --- |
| Yes | No | Location of partitions |
| Yes | No | Location and size of concealed spaces, closets, attics, and bathrooms |
| Yes | No | Full-height cross-sectional of structural and ceiling construction (Except 13D) |
| Yes | No | Location of fire walls (Except 13D) |

SPRINKLER COMPONENTS: Is the following information provided on plans/specification?

| Requirements For All Systems: |  |  |  |
| --- | --- | --- | --- |
| Yes | No |  | Make, type, model, nominal K-factor of sprinklers, and sprinkler identification number |
| Yes | No |  | Temperature rating and location of high-temperature sprinklers |
| Yes | No |  | Pipe type and schedule of wall thickness |
| Yes | No |  | Nominal pipe size and cutting lengths of pipe (or center-to-center dimensions) |
| Yes | No |  | Location and size of riser nipples |
| Yes | No |  | Type of fittings and joints and location of all welds and bends |
| Yes | No |  | Specifications of any sections to be shop welded and type of fittings or formations to be used |
| Yes | No |  | Type and location of hangers, sleeves, braces, and methods of securing sprinklers when applicable |
| Yes | No |  | All control valves, check valves, drain pipes, and test connections |
| Yes | No |  | Manufacturer, size, type of backflow preventers |
| Yes | No |  | Is a pressure gauge indicated on the system and the supply |
| Yes | No | N/A | Make, type, model, and size of alarm, dry pipe, preaction, or deluge valves |
| Yes | No | N/A | Size and location of standpipe risers, hose outlets, hand hose, monitor nozzles, and related equipment |
| Yes | No | N/A | Calculation of loads for sizing and details of sway bracing |
| Yes | No | N/A | Setting for pressure-reducing valves |
| Yes | No | N/A | Type and amount of antifreeze solution used |
| Additional Requirements For 13R Systems |  |  |  |
| Yes | No | N/A | If there is a separate control valve for the sprinkler system, is it supervised |
| Additional Requirements For 13D Systems |  |  |  |
| Yes | No | N/A | If an FDC is provided, pipe meets the minimum pressure rating |
| Yes | No | N/A | If there is a separate control valve for sprinkler system it is supervised |
| Yes | No | N/A | If a pressure tank is used, a pressure gauge installed to indicate tank pressure |
| Yes | No | N/A | If the system is dry, a pressure gauge indicated on the system to indicate air pressure |

FIRE DEPARTMENT CONNECTION(S), ALARMS, FIRE HYDRANTS

Is the following information provided on plans/specification?

| Required for All Systems: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Yes | No |  | Size, location, and piping arrangement of fire department connections |  |
| Yes | No |  | Size and location of hydrants (showing size and number of outlets and whether outlets to be equipped with independent gate valves) |  |
| Yes | No |  | Kind and location of alarm bells |  |
| Yes | No | N/A | Fire alarm system connection |  |
| Additional Requirements For 13 Systems |  |  |  |  |
| Yes | No | N/A | Whether hose houses and equipment are to be provided |  |
| Yes | No | N/A | If the system is a multipurpose piping system, a sign warning of water restricting devices is specified |  |
| Additional Requirements For 13R Systems |  |  |  |  |
| Yes | No | N/A | For building exceeding 2,000 ft2or greater than a single story, the size, location, and piping arrangement of the fire department connections indicated |  |

NOTES / ADDITIONAL COMMENTS: